Schedule of Technical Data

(All information requested under the Contractor’s Offer column are mandatory. Failure to provide the information will subject to the submission being disqualified.)

| Description | Tender Specifications | Bidder’s Offer |
| --- | --- | --- |
| Cooling Tower | New |  |
| General |  |  |
| Manufacturer | Nihon Spindle/Truwater/ or Approved Equivalent |  |
| Country of Manufacture | Malaysia |  |
| Type | Rectangular Induced Draft Cross Flow |  |
| Model | To state |  |
| No.of Cells | 2 |  |
| Overall Dimension | To suit site |  |
| Total Operating Weight | To state |  |
| Performance |  |  |
| Total Heat Rejection Capacity (HRT) | To state |  |
| Water Flow rate (usgpm) |  |  |
| Entering Water Temp (F) | 97 |  |
| Leaving Water Temp (F) | 87 |  |
| Wet Bulb Temperature (F) | 81 |  |
| Evaporation Loss | <0.84 % of circulating flowrate |  |
| Drift Loss | <0.02 % of circulating flow rate |  |
| Material of Construction |  |  |
| Casing | FRP |  |
| Structure/framework | HDGS |  |
| In-fills | PVC |  |
| Drift Eliminators | PVC |  |
| Hot Water Basin | FRP |  |
| Cold Water Basin | FRP |  |
| Fan Blade | Aluminium Alloy |  |
| Fan Cylinder | FRP |  |
| Drive System |  |  |
| Type of Drive | Belt and Pulley |  |
| Motor Type | TEFC Squirrel Cage IP55 |  |
| Motor Make | To state |  |
| Rated Power | To state |  |
| Rated Speed | 1450 rpm |  |
| Full Load Current | To state |  |
| Starting Current | To state |  |
| Electrical Characteristics | 415V/3ph/50Hz |  |
| Motor Efficiency | To state |  |
| Power Factor at F.L. | > 0.85 |  |
| Insulation Class | To state |  |
| Fan |  |  |
| Type of Fan | Axial flow |  |
| Fan Diameter | To state |  |
| Fan Speed | To state |  |
| Fan Tip Speed | To state |  |
| Piping Interface |  |  |
| Hot Water Inlet diameter | To state |  |
| Cold Water Discharge diameter | To state |  |
| Make-up Water Inlet diameter | To state |  |
| Drain Water Discharge diameter | To state |  |
| Balancing Pipe diameter | To state |  |

COMPANY’S STAMP AND AUTHORIZED SIGNATURE

……………………………………………………………….

DATE :