| ITEM NOS. | #### DESCRIPTION OF EQUIPMENT/SERVICES/WORKS | QTY | UNIT PRICE (RM) | TOTAL PRICE (RM) |
| --- | --- | --- | --- | --- |
| 1.0 1.1 1.2 1.3 2.0 2.1 3.0 3.1 3.2 3.2.1 3.2.2 3.2.3 3.2.4 3.2.5 3.2.6 3.2.7 3.2.8 3.2.9 3.2.10 3.2.11 | PRELIMINARY & MOBILIZATION Mobilization of qualified and experienced staff to do site survey, installation, testing and commissioning works with relevant tools. Provision for necessary tools and manpower to design and prepare CAD drawings for the purpose of management review and approval, submission to authorities, and compilation of operation manuals Full compliance to the statutory regulations and MIMOS OSH, Housekeeping and Security requirements in undertaking the job. STUDY & DESIGN To engage a consultant to undertake the study on the present load and distribution circuits, and to propose the new MSB 1B, and provision for alternative supply for 1000A Production SSB TECHNICAL REQUIREMENT Supply, deliver, install, test and commission the new 4000A MSB system which comprise of the following: MSB 1B 1 unit floor standing MSB w 4000A 85KA 3P Draw out ACB c/w S/T (Terasaki/ABB/Merlin Gerlin) SPAJ 140C E/F & O/C Relay ( ABB) 4000/5A Ammeter c/w S/SW (RELCO) 500V Volt meter c/w S/S/W (RELCO) P/F Meter ( RELCO) LED Phase Indicator lamp (HAROK) 6A Control fuse ( OVO) 4000/5A 10P10 Protection Current C/T (RELCO) 4000/5A Class 1 metering device C/T (RELCO) 60A 50KA 3P MCCB (LS) V25B+C/3+NPE Lighting Surge Arrestor Obobettermann) | 1 Lot 1 Lot 1 Lot 1 lot 1 lot 1 unit |  |  |

| ITEM NOS. | #### DESCRIPTION OF EQUIPMENT/SERVICES/WORKS | QTY | UNIT PRICE (RM) | TOTAL PRICE (RM) |
| --- | --- | --- | --- | --- |
| 3.3 3.3.1 3.3.2 3.3.3 3.3.4 3.3.5 3.3.6 3.3.7 3.3.8 3.3.9 3.4 3.5 3.6 3.7 3.8 3.8.1 3.8.2 | CAPACITOR BANK 2000A 65KA 3P Drawout ACB (Terasaki/ABB/Merlin Gerlin) 100A 37KA 3P MCCB ( Terasaki/ABB/Merlin Gerlin) 200A 37KA 3P MCCB (-ditto-) 100A Magnetic contactor 185A Magnetic Contactor 50KVAR 440V Capacitor (FRAKO) 100KVAR 440V Capacitor (FRAKO) 12 steps P/F/R (MIKRO) 6” Exhaust fans (TOYO) OUTGOING CIRCUITS (Please refer to the attached circuit) MCCB : (Terasaki/ABB/Merlin Gerlin) Cable size : To follow the IEEE standards in metal trunking. UPGRADING THE MSB1 To upgrade the bus bar for EMSB to get the supply from 1.5MVA Diesel gen set To upgrade all the breakers, protection devices, metering devices and circuits. LT BOARD (Transformer to MSB1 & MSB1B) To provide provision for 2 x 4000A Draw out ACB + Cabinet and necessary protection and metering devices from the 11kv/415v transformer ALTERNATE POWER SOURCE TO THE 1000A PRODUCTION SUBBOARD Provision to connect the STS to the existing 208V circuit, using approved type and size of PVC cables and isolation devices. 1 unit of 600KVA 415V/208V Stepped down transformer c/w DB and protection devices. | 1 lot 1 lot 1 lot 1 lot 1 lot 1 lot 1 lot 1 unit |  |  |

| ITEM NOS. | #### DESCRIPTION OF EQUIPMENT/SERVICES/WORKS | QTY | UNIT PRICE (RM) | TOTAL PRICE (RM) |
| --- | --- | --- | --- | --- |
| 3.8.3 3.8.4 3.8.5 3.9 3.9.1 3.10 3.10.1 3.10.2 3.10.3 3.10.4 | Provision to connect the 600KVA 415V/208V Stepped down transformer to the MSB 1 and to the STS. Supply and install sub board with Proper power rating and cabling works + protection devices for: i. Production equipment ii. MSB 1 iii. External gen set connection Provision of wiring works to connect the following sub switch board to the external gen set: i. Chiller SSB ii. MSB1 SSB MATERIALS & FINISHES FOR CABINET The frame and panels shall be constructed on corrosion resistant sheet steel to match the present thickness. The cabinet shall be powder coated to match the existing MSB1 colour. The rear panel shall be a dismantle-type OTHERS To provide necessary signage, labeling of circuits, manual of operation (2 sets) and relevant drawings ( 2 sets) upon successful commissioning of the new installation. To provide training (OJT and classroom) to MIMOS technical personnel involve in the installation, operation and maintenance of the new installation. To prepare relevant drawings/documentation to the relevant authorities, with copy for MIMOS To provide warranty for a period of 12 months after acceptance against any defect in workmanship. | 1 lot 1 lot 1 lot 1 lot 1 lot 1 lot 1 lot 1 lot |  |  |
|  | Total Amount (1.0 + 2.0 + 3.0 + 3.1 + 3.2 + 3.3 + 3.4 + 3.5 + 3.6 + 3.7 + 3.8 + 3.9 + 3.10) | - |  |  |